Motion services

# ABB Energy Appraisal

Energy Savings Potential

| Information |  |
| --- | --- |
| Customer | ION EXCHANGE |
| Plants | India |
| Data Source | Customer Input |
| Date of Report | 09.19.2025 |
| # of Assets | 11 / 18 |
| Electricity Cost | 8.00 INR/kWh |
| Carbon Intensity | 0.54 kg CO2/kWh |
| Tax Rate | 34.9% |

Content

Background	3

Summary	4

Energy savings with ABB premium efficiency solutions – Top 10	5

Application Details	6

Appendix	8

Application Details	8

Details of Recommendation	9

Calculation Methodology	13

NPV Methodology	15

# Background

| Background | This report has been produced to estimate the energy savings that might be gained from fitting or changing to modern energy efficient equipment. It has been generated using available data to highlight potential energy saving applications. It may be necessary to carry out deeper analysis to properly assess the exact savings that can be made. The report highlights applications which will benefit from fitting energy efficient motors and variable speed drives |
| --- | --- |
| Disclaimer | The information contained in the final report will be indicative only as outlined in the Service Description and the customer must make its own assessment of the final report and its own circumstances rather than solely relying on ABB’s report. ABB and its affiliates make no representations, warranties or provide guarantees of any kind, whether express, implied, statutory or otherwise, including without limitation in respect of performance outcomes, fitness for purpose, satisfactory quality, and any warranties arising out of any course of dealing or usage of trade. Except to the extent prohibited by applicable law, ABB expressly disclaims any such representations, warranties or guarantees. Except to the extent prohibited by applicable law, (i) ABB’s liability for direct damages is limited to USD100 (US Dollar one hundred) or value of purchase order, whichever is lower and (ii) ABB is not liable in any amount for an special, punitive, incidental, consequential or indirect damages or loss including, without limitation, loss of profit, loss of revenue, loss of goodwill, loss of use, loss of production, anticipated savings, business interruption, loss or compromise of data, however arising and regardless of the basis of the claim. |
| Terms & Conditions | ABB Energy Appraisal Terms and Conditions |

# Summary

| INR 3,312,551 Annual energy cost savings* |  | Annual energy consumption* | 11/18 motors NPV positive |
| --- | --- | --- | --- |
| Business Case |  |  |  |
| 4.7 yrs Payback time – Top 10* |  | Payback time sensitivity to electricity price variation* | INR 12,015,351 Net Present Value* |
| INR 15,679,593 Investment cost* |  |  | 16% Internal rate of return – Top 10* |
| Sustainability |  |  |  |
| 224 tCO2 Annual CO2 avoided* | 118 Vehicles Savings in kWh equal the annual operation of Battery Electric Vehicles* Assuming annual battery operation of 3.500kWh annually |  | Credit Voucher & Report via Take-back Program |

*Only considering the NPV positive assets

# Energy savings with ABB premium efficiency solutions – Top 10

| # | Application | Energy. Cons (kWh) | Energy Cost (INR) | CO2 Cons. (kg) | Energy Savings (kWh) | Investment (INR) | Energy Cost Savings (INR) | Energy Savings (%) | Payback time (years) | Avoided CO2 (kg) | Takeback Available |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | HRSC-LCP-201 | 39,773 | 318,182 | 21,477 | 5,337 | 130,816 | 42,696 | 13% | 3.1 | 2,882 | ✓ |
| 9 | IUD-PM-06A | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 10 | IUD-PM-06B | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 11 | IUD-PM-06C | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 12 | IUD-PM-06D | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 13 | IUD-PM-06E | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 14 | IUD-PM-06F | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 15 | IUD-PM-06G | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 16 | IUD-PM-08A | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| 17 | IUD-PM-08B | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 6% | 4.8 | 22,072 | ✓ |
| Total Energy- Top 10 Saving Assets |  | 6,481,841 | 51,854,730 | 3,500,194 | 373,196 | 14,124,716 | 2,985,566 | 6% | 4.7 | 201,526 | ✓ |
| Total NPV Positive Assets (11) |  | 7,197,627 | 57,581,013 | 3,886,718 | 414,069 | 15,679,593 | 3,312,551 | 6% | 4.7 | 223,597 | ✓ |

*Data is listed as total annual figures

# Application Details

| # | Application | IE | Driven load | Flow control method | Connection | Output (kW) | Shaft height (Frame) | Running time (hours) | Avg. Flow (%) or Avg. Frequency (Hz) | Recommended ESS motor | ESS connection |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | HRSC-LCP-201 | 1 | Centrifugal Pump | Information not available | VSD | 7.5 | 320 | 7920 | 40.0 | M3AL 132SMB 4 ¦ 7.5 kW ¦ IE5 ¦ Shaft: 132 ¦ 415 V ¦ 50.0 Hz ¦ SynRM Motors | ACS580-01-018A-4+B063 |  |
| 9 | IUD-PM-06A | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 10 | IUD-PM-06B | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 11 | IUD-PM-06C | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 12 | IUD-PM-06D | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 13 | IUD-PM-06E | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 14 | IUD-PM-06F | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 15 | IUD-PM-06G | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 16 | IUD-PM-08A | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |
| 17 | IUD-PM-08B | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |  |

Notes on Payback

The ABB payback calculations are made taking into consideration typical system inefficiencies and savings which are in fact present when using dampers or restrictors. In short, they are a realistic payback calculation based on several years’ experience, not just the implementation of the simple 'cube law' rules which can give exaggerated, unachievable results, with paybacks that are too short.

NPV

NPV is calculated assuming a discount rate of 6.5%, a useful life of 20 years and depreciation of the assets during 10 years, a constant electricity price and country corporate tax rate.

# Appendix

## Application Details

| # | Application | Energy Cons. (kWh) | Energy Cost (INR) | CO2 Cons. (kg) | Energy Savings (kWh) | Investment (INR) | Energy Cost Savings (INR) | Payback Time (years) | Avoided CO2 (kg) | Energy Savings (%) | NPV |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | HRSC-LCP-201 | 39,773 | 318,182 | 21,477 | 5,337 | 130,816 | 42,696 | 3.1 | 2,882 | 13% | 208,264 |
| 2 | IUD-PM-07A | 562,397 | 4,499,172 | 303,694 | -30,202 | 0 | -241,612 |  | (16,309) | -5% | (1,733,095) |
| 3 | IUD-PM-07B | 562,397 | 4,499,172 | 303,694 | -30,202 | 0 | -241,612 |  | (16,309) | -5% | (1,733,095) |
| 4 | IUD-PM-07C | 562,397 | 4,499,172 | 303,694 | -30,202 | 0 | -241,612 |  | (16,309) | -5% | (1,733,095) |
| 5 | IUD-PM-07D | 562,397 | 4,499,172 | 303,694 | -30,202 | 0 | -241,612 |  | (16,309) | -5% | (1,733,095) |
| 6 | IUD-PM-07E | 562,397 | 4,499,172 | 303,694 | -30,202 | 0 | -241,612 |  | (16,309) | -5% | (1,733,095) |
| 7 | IUD-PM-07F | 562,397 | 4,499,172 | 303,694 | -30,202 | 0 | -241,612 |  | (16,309) | -5% | (1,733,095) |
| 8 | IUD-PM-07G | 562,397 | 4,499,172 | 303,694 | -30,202 | 0 | -241,612 |  | (16,309) | -5% | (1,733,095) |
| 9 | IUD-PM-06A | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 10 | IUD-PM-06B | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 11 | IUD-PM-06C | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 12 | IUD-PM-06D | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 13 | IUD-PM-06E | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 14 | IUD-PM-06F | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 15 | IUD-PM-06G | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 16 | IUD-PM-08A | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 17 | IUD-PM-08B | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |
| 18 | IUD-PM-08C | 715,785 | 5,726,283 | 386,524 | 40,873 | 1,554,878 | 326,986 | 4.8 | 22,072 | 6% | 1,180,709 |

## Details of Recommendation

More information about the various devices can be found here: www.abb.com/motors-generators

This section contains an overview of the new fleet with the changes implemented. Each application has been individually reported. The following applications were inspected:

| # | Application | IE | Driven load | Flow Control | Connection | Out-put (kW) | Shaft height (Frame) | Running time (hours) | Avg. Flow (%) or Avg. Frequency (Hz) | Recommended ESS motor | ESS connection |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | HRSC-LCP-201 | 1 | Centrifugal Pump | Information not available | VSD | 7.5 | 320 | 7920 | 40.0 | M3AL 132SMB 4 ¦ 7.5 kW ¦ IE5 ¦ Shaft: 132 ¦ 415 V ¦ 50.0 Hz ¦ SynRM Motors | ACS580-01-018A-4+B063 |
| 2 | IUD-PM-07A | 1 | Centrifugal Pump | Information not available | VSD | 125.0 | 320 | 7920 | 40.0 | M3BP 315SMC 2 ¦ 132.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-240A-5 |
| 3 | IUD-PM-07B | 1 | Centrifugal Pump | Information not available | VSD | 125.0 | 320 | 7920 | 40.0 | M3BP 315SMC 2 ¦ 132.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-240A-5 |
| 4 | IUD-PM-07C | 1 | Centrifugal Pump | Information not available | VSD | 125.0 | 320 | 7920 | 40.0 | M3BP 315SMC 2 ¦ 132.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-240A-5 |
| 5 | IUD-PM-07D | 1 | Centrifugal Pump | Information not available | VSD | 125.0 | 320 | 7920 | 40.0 | M3BP 315SMC 2 ¦ 132.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-240A-5 |
| 6 | IUD-PM-07E | 1 | Centrifugal Pump | Information not available | VSD | 125.0 | 320 | 7920 | 40.0 | M3BP 315SMC 2 ¦ 132.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-240A-5 |
| 7 | IUD-PM-07F | 1 | Centrifugal Pump | Information not available | VSD | 125.0 | 320 | 7920 | 40.0 | M3BP 315SMC 2 ¦ 132.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-240A-5 |
| 8 | IUD-PM-07G | 1 | Centrifugal Pump | Information not available | VSD | 125.0 | 320 | 7920 | 40.0 | M3BP 315SMC 2 ¦ 132.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-240A-5 |
| 9 | IUD-PM-06A | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 10 | IUD-PM-06B | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 11 | IUD-PM-06C | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 12 | IUD-PM-06D | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 13 | IUD-PM-06E | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 14 | IUD-PM-06F | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 15 | IUD-PM-06G | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 16 | IUD-PM-08A | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 17 | IUD-PM-08B | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |
| 18 | IUD-PM-08C | 1 | Centrifugal Pump | Information not available | VSD | 160.0 | 320 | 7920 | 40.0 | M3BP 315MLA 2 ¦ 160.0 kW ¦ IE4 ¦ Shaft: 315 ¦ 415 V ¦ 50.0 Hz ¦ Super Premium Efficiency Cast Iron Motors | ACS880-01-260A-5 |

## Calculation Methodology

- All assets under VSD to VSD: Method A.

- All assets under DOL to VSD: Method B.

|  | Method A – Any driven equipment | Method B – pumps and fans | Method C – pumps and fans |
| --- | --- | --- | --- |
| Accuracy Level |  |  |  |
| Amount of Data Required | Least amount of data | Medium amount of data | Large amount of data |
| Brief description of method | This method uses the motor loading data. This loading data can be obtained through input power measurements, current measurements, or through smart sensor measurements. In the case of VSD-connected assets, method A uses the supply frequency to the motor to estimate the power consumption. | The calculation of the input power required is based on the flow rate data and control mechanism used, using power multipliers at different flow rates for each control mechanism. | In addition to flow rate and control mechanism data: For pumps, this method estimates the pump performance and system curves based on head and flow data from the pump. For fans, this method uses the total and static pressure to determine the required input power to the fan. |
| Calculation Steps | - Calculating the motor nominal efficiency, this is done based on the IE class and the nameplate information. - For DOL - calculating the estimated output power of the motor, based on the motor loading and motor rated power. This can be either extracted from Smart Sensors or a first estimate can be used just to have an idea of potential savings. For VSD the difference is that the output power is not determined from a motor loading input data (since this is not available for VSD-connected motors) but rather, the motor loading is estimated based on the operating speed of the motor (estimated from average supply frequency data from the VSD) and the type of load (variable or constant torque). - Calculating the real efficiency at load of the motor. The real losses and efficiency of the motor depend on the operating point, which is defined in terms of the motor loading at which the motor is operating. - Calculating the input power to the motor based on its output power and operational efficiency. - Estimating energy consumption, based on the input power and operating hours of the equipment. - Based on the previously described steps, energy consumption of the input asset and of the Energy Saving Solution are calculated, after which these are compared, and the energy savings are estimated. When the current asset and the ESS remain with the same type of connection, the same operating data may be used. However, when we are switching from a DOL type of connection to adding a VSD (i.e. using speed control) we need to be able to estimate what the new operating speed will be. This operating speed calculation when switching from DOL to VSD is slightly different depending on the type of load of the application. For pumps and fans, the flow control mechanism is considered. Given the current motor loading and type of flow control mechanism we can assume what is the current flow rate in the application. From there, assuming that the flow rate is proportional to the operating speed, we estimate what will be the required operating speed for the new electric motor which would be VSD-connected. | - Calculating the motor nominal efficiency, this is done based on the IE class and the nameplate information. - Calculating the motor loading at each of the operating flow rates at which the motor is running, based on the type of control mechanism (throttling, on/off, inlet vane, VSD, etc.). - Calculating the estimated output power of the motor, based on the motor loading and motor rated power. - Calculating the real efficiency at load of the motor. The real losses and efficiency of the motor depend on the operating point, which is defined in terms of the motor loading at which the motor is operating. - Calculating the input power to the motor based on its output power and operational efficiency. - Estimating energy consumption, based on the input power and operating hours of the equipment. - Energy savings are calculated same as Method A. - For DOL to VSD cases, using the input operating data from a DOL asset (usually flow rate histogram) can be directly applied to the VSD case, since we assume that flow rate (%) is equal to speed (%). Meaning that if the motor was running 50% of the time at 50% flow rate, it will now run 50% of the time at 50% speed. | - Calculating the motor nominal efficiency, this is done based on the IE class and the nameplate information. - Calculating the motor loading at each of the operating flow rates. This depends on which application we look at. For pumps: estimate the pump performance and system curves, which can then be used to estimate the head at different flow rates. With the flow rate data and type of flow control mechanism (throttling, on/off, VSD, etc.) the pump and system head are determined. Savings are obtained by reducing the ESS motor speed along the system curve. For fans: estimate the power required to run the fan at the given pressure difference, nominal flow rate, type of flow control mechanism (inlet vane, damper, VSD), type of impeller, type of fan (axial or centrifugal) and com-pression factor. - Calculating the estimated output power of the motor at the different flow rates that it is being used based on the parameters of the application. - Calculating the real efficiency at load of the motor. The real losses and efficiency of the motor depend on the operating point, which is defined in terms of the motor loading at which the motor is operating. - Calculating the input power to the motor based on its output power and operational efficiency. - Estimating energy consumption, based on the input power and operating hours of the equipment. - Energy savings are calculated same as Method A. |

## NPV Methodology

NPV is calculated assuming a discount rate of 6.5%, a useful life of 20 years and depreciation of the assets during 10 years, a constant electricity price and country corporate tax rate.

Calculations:

- Annual Cash Flow Calculation:
Annual Cash Flow is determined using the following formula:

Annual Cash Flow = Annual Cost Savings * (1 - Corporate Tax Rate) + Depreciation Shield Over 10 Years

- Annual Cost Savings: The yearly savings in energy costs.

- Corporate Tax Rate: Used to adjust savings after taxes.

- Depreciation Over 10 Years: Represents the tax benefit of asset depreciation.

- Depreciation Calculation:
Depreciation is calculated assuming a straight-line method over 10 years:

- Depreciation per Year = (Investment Cost * Tax Rate) / 10

- This depreciation amount is added to the annual cash flow as a non-cash tax shield.

- Net Present Value (NPV) Calculation:
NPV helps determine the project’s profitability by discounting future cash flows:

NPV = Σ [Annual Cash Flow / (1 + Discount Rate)^t], for t = 1 to 20

- Discount Rate: The rate used to bring future cash flows to present value.